ADDENDUM NO. 02 August 15, 2024

To Proposal Bid Package

DISTRICT-WIDE ACCESS CONTROL UPGRADES PACKAGE 3
CLOVIS UNIFIED SCHOOL DISTRICT

Notice to Bidders:
A. Receipt of this Addendum shall be acknowledged on the Bid Form.

B. This Addendum forms part of the Contract documents for the above referenced project and shall be incorporated integrally therewith.
C. Each bidder shall make necessary adjustments and submit his proposal with full knowledge of all

modifications, clarifications, and supplemental data included therein. Where provisions of the following supplemental data differ from those of the original Contract Documents, this Addendum shall govern.

DRAWINGS

CLOVIS WEST HIGH SCHOOL

Item No 01	Sheet 3-CWH-AC1 – Overall Site Plan

a.	Added Classroom Building ‘P’ to the project scope b.	Added Classroom Building ‘J’ to the project scope c.	Added Building ‘K’ to the project scope
d.	Added Building ‘B’ to the project scope

e.	Adjusted the shading of Building ‘C’ to the correct location

Item No 02	Sheet 3-CWH-AC2 – Administration Building

a.	Added CWH-BA-DR07 door to the project scope

b.	Adjusted the location of the existing IDF and new access control panel and homerun cabling routes from card reader doors back to new access control panel.

Item No 03	 Sheet 3-CWH-AC2.1 – Administration Building a.	Add sheet in its entirety.
b.	Added photos and door hardware information for CWH-BA-DR07 door.

Item No 04	Sheet 3-CWH-AC6 – Classroom Wing ‘S’ Building

a.	Adjusted the location of the existing IDF, existing electrical panel and new access control panel and homerun cabling routes from card reader doors back to new access control panel.

Item No 05	 Sheet 3-CWH-AC7 – Classroom Wing ‘S’ Building Photos a.	Updated photos of existing electrical panel
b.          Updated photos of CWH-BCW-DR01 door and hardware set c.           Updated photos of CWH-BCW-DR02 door and hardware set

Item No 06	Sheet 3-CWH-AC8 – East Gym

a.	Removed CWH-BEG-DR04 (weight room) door from project scope

Page	of 4

b.	Adjusted the location of the existing IDF and new access control panel and homerun cabling routes from card reader doors back to new access control panel.

Item No 07	 Sheet 3-CWH-AC9 – East Gym - Photos a.	Updated photos of existing IDF

Item No 08	Sheet 3-CWH-AC10 – East Gym - Photos

a.	Removed photos and references to weight room door CWH-BEG-DR04.

Item No 09	Sheet 3-CWH-AC12 – Classroom Building ‘C’

a.	Adjusted the location of the existing IDF, existing electrical panel and new access control panel and homerun cabling routes from card reader doors back to new access control panel.

Item No 10	 Sheet 3-CWH-AC13 – Classroom Building ‘C’ - Photos a.	Updated photos of existing electrical panels

Item No 11	Sheet 3-CWH-AC14 – Classroom Building ‘C’ - Photos

a.	Updated photos of CWH-BC-DR03 doo and hardware set

Item No 12	Sheet 3-CWH-AC15 – Library

a.	Adjusted the location of the existing electrical panel

Item No 13	Sheet 3-CWH-AC17 – West Gym Plan

a.	Added CWH-BWG-DR14 to the project scope b.	Added CWH-BWG-DR15 to the project scope c.	Added CWH-BWG-DR16 to the project scope d.	Added CWH-BWG-DR17 to the project scope e.	Added CWH-BWG-DR18 to the project scope
f.	Adjusted locations of existing IDF and existing electrical panels.

g.	 Showed homerun cabling routes for doors leading back to each of the new access control panel locations. Split cable routing between Boys and Girls Coaches Office locations as shown.
h.	Added additional Request to Exit devices in gym. One REX is associated with each pair of doors.

Item No 14	Sheet 3-CWH-AC18 – West Gym - Photos

a.	Added photos of Boys and Girls Coaches Office IDF locations

Item No 15	Sheet 3-CWH-AC19 – West Gym - Photos

a.	Adjusted door hardware schedules for DR01, DR02 and DR03 doors.

Item No 16	Sheet 3-CWH-AC20 – West Gym - Photos

a.	Adjusted door hardware schedules for DR04, DR05 and DR06 doors.

Item No 17	Sheet 3-CWH-AC21 – West Gym - Photos

a.	Updated photos and hardware for CWH-BWG-DR07.

Item No 18	Sheet 3-CWH-AC22 – West Gym - Photos

Page	of 4

a.	Updated door hardware schedules for DR10, DR11 and DR12. b.	Updated photos of CWH-BWG-DR12.

Item No 19	Sheet 3-CWH-AC23 – West Gym - Photos

a.          Updated photos of CWH-BWG-DR013 and hardware set. b.          Updated photos of CWH-BWG-DR014 and hardware set c.           Updated photos of CWH-BWG-DR015 and hardware set

Item No 20	 Sheet 3-CWH-AC23.1 – West Gym - Photos a.	Added sheet in its entirety.
b.          Updated photos of CWH-BWG-DR016 and hardware set. c.           Updated photos of CWH-BWG-DR017 and hardware set d.          Updated photos of CWH-BWG-DR018 and hardware set

Item No 21	Sheet 3-CWH-AC24 – Multi-Purpose Building Plan

a.          Added door CWH-BMPR-DR08 to project scope b.          Added door CWH-BMPR-DR09 to project scope
c.	Adjusted the location of the existing IDF, existing electrical panel and new access control panel and homerun cabling routes from card reader doors back to new access control panel.

Item No 22	 Sheet 3-CWH-AC27 – Multi-Purpose Building Photos a.	Updated photos of door CWH-BMPR-DR06.
b.	Updated photos of existing MPR IDF room.

Item No 23	 Sheet 3-CWH-AC28 – Multi-Purpose Building Photos a.	Add sheet in its entirety.
b.	Added photos of door CWH-BMPR-DR08 and hardware set. c.	Added photos of door CWH-BMPR-DR09 and hardware set. d.	Added photos of existing electrical room

Item No 24	 Sheet 3-CWH-AC29 – Building ‘B’ Plan a.	Add sheet in its entirety.
b.	Added new Building ‘B’ floor plan and door photos and hardware set.

Item No 25        Sheet 3-CWH-AC30 – Classroom Building ‘J” a.          Add sheet in its entirety.
b.	Added new Building ‘J’ floor plan

c.	Add photos of existing electrical room d.	Add photos of existing IDF room

Item No 26	 Sheet 3-CWH-AC31 – Classroom Building ‘J” Photos a.	Add sheet in its entirety.
b.	Added overall layout of building

c.           Added photos of door CWH-BJ-DR01 and hardware set d.          Added photos of door CWH-BJ-DR02 and hardware set

Item No 27	 Sheet 3-CWH-AC32 – Classroom Building ‘J” Photos a.	Add sheet in its entirety.

Page	of 4

b.          Added photos of door CWH-BJ-DR03 and hardware set c.           Added photos of door CWH-BJ-DR04 and hardware set

Item No 28	 Sheet 3-CWH-AC33 – Building ‘K’ Plan a.	Add sheet in its entirety.
b.	Added overall layout of building

c.	Added photos of door CWH-BK-DR01 and hardware set d.	Added photos of door CWH-BK-DR02 and hardware set e.	Added photos of existing electrical room and IDF room

Item No 29	 Sheet 3-CWH-AC34 – Classroom Building ‘P’ Plan a.	Add sheet in its entirety.
b.	 Overall layout of building and location of doors, electrical and IDF room along with homerun routing of cabling back to new access control panel.

Item No 30	 Sheet 3-CWH-AC35 – Classroom Building ‘P’ Photos a.	Add sheet in its entirety.
b.	Added photos of overall building

c.           Added photos of door CWH-BP-DR01 and hardware set d.          Added photos of door CWH-BP-DR02 and hardware set

Item No 31	 Sheet 3-CWH-AC36 – Classroom Building ‘P’ Photos a.	Add sheet in its entirety.
b.	Added photos of existing electrical room c.	Added photos of existing IDF room

End of Addendum 02

Page	of 4

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER

ACCESS CONTROL - GENERAL NOTES:

ALL LOW VOLTAGE CABLING IN EXPOSED AREAS SHALL BE INSTALLED IN SURFACE MOUNTED RACEWAY OR CONDUIT

ALL EXPOSED CONDUIT IN PUBLIC SPACES SHALL BE PAINTED TO MATCH EXISTING WALL OR CEILING COLOR

ALL ACCESS CONTROL WIRING SHALL BE GREEN IN COLOR

ALL LOW VOLTAGE WIRING NOT INSTALLED IN CONDUIT SHALL BE SUPPORTED EVERY 5' MINIMUM FROM APPROVED CABLING SUPPORT SYSTEM CONNECTED BACK TO BUILDING STRUCTURE

COORDINATE WITH OWNER TECHNOLOGY DEPARTMENT ON LABELING AND TERMINATION PUNCHDOWN OF NEW DATA CABLING ASSOCIATED WITH ACCESS CONTROL SYSTEM

CONTRACTOR TO REPAIR ANY HOLES IN EXISTING DOORS AND FRAMES AS A RESULT OF HARDWARE REPLACEMENT. CONTRACTOR TO REPAINT FRAMES AND DOORS TO MATCH EXISTING SURROUNDING COLOR FOR ANY AREAS EXPOSED WHERE OLD HARDWARE WAS REMOVED.

CONTRACTOR TO COORDINATE WITH OWNER ON ALL PROGRAMMING AND DOOR NUMBERING REQUIREMENTS ASSOCIATED WITH ACCESS CONTROL SYSTEM PRIOR TO ANY WORK TAKING PLACE

CONTRACTOR IS RESPONSIBLE FOR PROVIDING BUILDING MAPS FOR EACH CAMPUS BUILDING AND INTEGRATING WITH ACCESS CONTROL DOOR LOCATIONS TO INDICATE DOOR STATUS AND PROVIDE REMOTE OPERATION OF DOORS THRU ACCESS CONTROL SYSTEM

CONTRACTOR IS REQUIRED TO PROVIDE ALL DOOR HARDWARE, WIRING AND POWER SUPPLIES ASSOCIATED WITH THE INSTALLATION OF ACCESS CONTROL SYSTEM.

CONTRACTOR TO PROVIDE 120V. POWER, CONDUIT, WIRING AND BREAKERS ASSOCIATED WITH PROVIDING POWER TO ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES

CONTRACTOR SHALL COORDINATE WITH OWNER ON THE TRANSITION AND SCHEDULING OF ACCESS CONTROL SYSTEM ONCE ITS READY TO ACTIVATE FOR EACH BUILDING

CONTRACTOR SHALL MAINTAIN EXISTING WALL RATINGS FOR ANY PENETRATIONS THRU EXISTING RATED WALLS AS A RESULT OF ANY NEW CABLING BEING INSTALLED.

CONTRACTOR SHALL INSTALL A REQUEST TO EXIT "REX" DEVICE FOR ALL DOORS RECEIVING A CARD READER AND ELECTRIFIED HARDWARE INTERFACE. REX DEVICE SHALL PROVIDE STATUS OF BOTH DOORS. DEVICE TO BE WALL OR CEILING MOUNTED TO PROVIDE PROPER COVERAGE OF EXIT PATHWAY

ACCESS CONTROL - KEYED NOTES:

1

2

3

4

5

6

7

8

9

10

11

THIS DOOR SHALL RECEIVE A NEW CARD READER. CONTRACTOR SHALL REFER TO DOOR HARDWARE SCHEDULE FOR WORK SCOPE REQUIRED. PROVIDE ALL NEW HARDWARE, WIRING AND TERMINATIONS REQUIRED TO INSTALL NEW CARD READER AND ELECTRIFIED DOOR HARDWARE

LOCATION OF EXISTING MDF/IDF ROOM. ALL NEW ACCESS CONTROL PANELS AND DOOR POWER SUPPLIES SHALL BE INSTALLED IN THIS ROOM.

LOCATION OF NEW ACCESS CONTROL PANEL AND DOOR POWER SUPPLIES SHALL BE MOUNTED ON THE WALL AT THIS LOCATION. CONTRACTOR TO INSTALL NEW CATEGORY 6 DATA CABLE FROM NEW ACCESS CONTROL PANEL BACK TO EXISTING PATCH PANEL IN EXISTING DATA RACK AND TERMINATE ON AVAILABLE PORT. CONTRACTOR TO INSTALL NEW WIRING IN SURFACE MOUNTED RACEWAY OR ROUTED ON EXISTING LADDER RACK FROM ACCESS CONTROL PANEL BACK TO RACK. CONTRACTOR TO INSTALL NEW 120V, 20A DUPLEX RECEPTACLE IN ACCESS CONTROL PANEL AND CONNECT BACK TO EXISTING ELECTRICAL PANEL

FRONT ADMINISTRATION AREA TO RECEIVE NEW WALL MOUNTED LOCKDOWN BUTTON WITH COVER IN THIS AREA. COORDINATE WITH OWNER ON FINAL LOCATION OF BUTTON PRIOR TO INSTALLATION. CONTRACTOR TO PROVIDE LABELING OF BUTTON TO INDICATE "LOCKDOWN" ON COVER. BUTTON SHALL BE BLUE IN COLOR.

APPROXIMATE ROUTE OF MULTICONDUCTOR ACCESS CONTROL CABLE FROM ACCESS CONTROL DOOR BACK TO HEADEND PANEL LOCATED IN MDF/IDF ROOM. CONTRACTOR SHALL BE RESPONSIBLE FOR ALL NEW RACEWAY OR ACCESS PANELS REQUIRED TO INSTALL ACCESS CONTROL WIRING ABOVE INACCESSIBLE CEILINGS. ALL WIRING SHALL BE PROPERLY SUPPORTED FOR FULL RUN. ANY WIRING PENETRATIONS PASSING THRU RATED WALL SHALL MAINTAIN WALL RATING AFTER WIRING IS INSTALLED.

LOCATION OF EXISTING 120V ELECTRICAL PANEL. CONTRACTOR TO ROUTE NEW 120V, 20A BRANCH CIRCUIT FROM NEW ACCESS CONTROL PANEL BACK TO THIS LOCATION. CONTRACTOR SHALL INSTALL NEW 120V, 20A BREAKER IN AVAILABLE SPACE IN THIS PANEL.

LOCATION OF EXISTING FLOOR MOUNTED NETWORK RACKS. ALL NEW DATA CABLING SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON EXISTING PATCH PANEL.

LOCATION OF EXISTING INTERCOM WALL MOUNTED PUNCHDOWN BLOCK. ALL NEW SPEAKERS SHALL BE ROUTED BACK TO THIS LOCATION AND TERMINATED ON TERMINAL STRIP. CONTRACTOR TO CONFIGURE EXISTING INTERCOM SYSTEM TO ADD ANY NEW EXTERIOR SPEAKER AND ZONES TO EXISTING SYSTEM AS REQUIRED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE,
NON-POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION.

THIS AREA HAS AN OPEN CEILING AREA OR INACCESSIBLE CEILING AREA, CONDUIT WILL BE REQUIRED TO ROUTE THRU OPEN AREAS OR ACCESS PANELS NEEDED TO ACCESS ABOVE INACCESSIBLE CEILINGS TO ALLOW CABLING TO BE INSTALLED.

CONTRACTOR TO INSTALL NEW WALL MOUNTED, EXTERIOR GRADE, POWERED SPEAKER, WHITE IN COLOR AT THIS LOCATION AND CONNECT BACK TO EXISTING LOCAL BUILDING INTERCOM TERMINAL STRIP AT EXISTING MDF/IDF LOCATION. PROVIDE LOCAL POWER TRANSFORMER AND TERMINATIONS REQUIRED TO POWER SPEAKER